## Slide 1: بسم الله الرحمن الرحيم PID Controllers
Action, types and tuning
Ref 1: Smith & Corripio “Principles and practice of automatic process control”, 3rd ed., Wiley, 2006, Chapter 5 & 7.
Ref 2: Yu, Autotuning of PID controllers, 2nd ed., Springer, 2006, Chapters 2 &3.
Ref 3: Vilanova & Visioli “PID control in the third millennium, Springer, 2012, Chapter 5.

## Slide 2: 1- Action of PID Controllers
If the action is not correctly selected, the controller will not control
Reverse action (increase/decrease)
In feedback control loop, the multiplication of Process gain (Kp), Control valve gain (Kv), Sensor gain (Km) and Controller gain (Kc) must be positive.
Reverse action : If Kp Kv Km > 0 → Kc > 0

## Slide 3: 1- Action of PID Controllers
Direct action (increase/increase)
To determine the action of a controller, the engineer must know:
The process characteristics
The fail-safe action of the control valve
Direct action : If Kp Kv Km < 0 → Kc < 0

## Slide 4: 2- Types of PID Controllers
  Classic PID:
  Parallel PID (Ideal PID):
  Series PID:
Range :
0.01 to 0.2
(0.1)

## Slide 5: 2- Types of PID Controllers

## Slide 6: 3- Problems and Modifications of PID Controllers
Reset Windup

## Slide 7: 3- Problems and Modifications of PID Controllers
Reset Feedback (RFB)
Internal Reset Feedback

## Slide 8: 3- Problems and Modifications of PID Controllers
Reset Feedback (RFB)

## Slide 9: 3- Problems and Modifications of PID Controllers
Reset Feedback (RFB)
External Reset Feedback

## Slide 10: 3- Problems and Modifications of PID Controllers
Proportional and Derivative Kick
Proportional Kick
Derivative Kick
Range: 0-1
Range: 0-1, Commonly zero
Two Degrees of Freedom or ISA - PID

## Slide 11: 3- Problems and Modifications of PID Controllers

## Slide 12: 4- Tuning of PID Controllers
Ziegler-Nichols (1942): Recommended for 0.1< D/t <0.5 ( )
More than 250 tuning rules are exist for PI and PID Controllers
What is the suitable tuning rule?
It really depends on your process (Type, Order, Parameters, Nonlinearity, Uncertainty, etc)

## Slide 13: 4- Tuning of PID Controllers
Tyreus-Luyben (1992): Recommended for time-constant dominant processes ( D/t <0. 1 )
Ciancone-Marlin (1992): Recommended for dead-time dominant processes ( D/t > 2.0 )

## Slide 14: 4- Tuning of PID Controllers
PID tuning based on IMC (Rivera et al., 1986)
Method | Kc | tI | l
SIMC |  |  | D
ISIMC |  |  | D

## Slide 15: 5- Model Identification (Open-loop step test)
Final Control Element
Process
Sensor/ Transmitter
Step Change
Record
m(t), %
c(t) , %
Process Gain:

## Slide 16: 5- Model Identification (Open-loop step test)
Fit 1 :

## Slide 17: 5- Model Identification (Open-loop step test) 4
Fit 2 :

## Slide 18: 5- Model Identification (Open-loop step test)
Fit 3 :

## Slide 19: 5- Model Identification (Close-loop ZN)
Ziegler-Nichols Test (1942)
Set the controller gain Kc at a low value, perhaps 0.2.
Put the controller in the automatic mode.
Make a small change in the set point or load variable and observe the response. If the gain is low, then the response will be sluggish.
Increase the gain by a factor of two and make another set point or load change.
Repeat step 4 until the loop becomes oscillatory and continuous cycling is observed. The gain at which this occurs is the ultimate gain Ku , and the period of oscillation is the ultimate period Pu.

## Slide 20: 5- Model Identification (Relay feedback test)
Relay Feedback Test (Astrom & Hagglund, 1984)
Luyben popularized relay feedback method and called this method “ATV” (autotune variation).

## Slide 21: 5- Model Identification (Relay feedback test)

## Slide 22: 5- Model Identification (Relay feedback test)
Advantages of Relay Feedback Test
It identifies process information around the important frequency, the ultimate frequency (where the phase angle is -π).
It is a closed-loop test; therefore, the process will not drift away from the nominal operating point.
The amplitude of oscillation is under control (by adjusting h ).
The time required for a relay feedback test is roughly equal to two to four times the ultimate period.
If the normalized dead time D /t is less than 0.28, the ultimate period is smaller than the process time constant. Therefore the relay feedback test is more time efficient than the step test. Since the dead time can not be too large, the temperature and composition loops in process industries seem to fall into this category.

## Slide 23: 5- Model Identification (Relay feedback test)
Advantages of Relay Feedback Test

## Slide 24: 5- Model Identification (Close-loop step test)
Shamsuzzoha and Skogestad, 2010
Yuwana and Seborg, 1982, proposed a modification to the Ziegler-Nichols closed-loop experiment. Instead of bringing the system to its limit of stability, one uses a P-controller with a gain that is about half this value, such that the resulting overshoot to a step change in the setpoint is about 30%.This method was modified by Shamsuzzoha and Skogestad, 2010.

## Slide 25: 5- Model Identification (Close-loop step test)
Kc : Controller gain used in experiment
ys : Set point change
tp : First peak time
yp : Maximum output change
y : Steady state output change